## Site parameters
Site and plant parameters
Average water depth at site | 22.5 | m
Distance between port and site | 124 | km
Distance between cable landfall and offshore substation | 42 | km
Distance between cable landfall and cabling vessel anchor point | 0 | km
Distance between cable landfall and onshore interconnection point | 3 | km
Number of turbines | 50 | turbines
Spacing between turbines in a string | 7 | rotor diameters
Spacing between strings | 9 | rotor diameters
Distance from offshore substation to first turbine on each string | 1 | km
Total plant capacity | 400 | MW
Number of export cables | 2 | cables

## 8MW turbine parameters
8MW turbine parameters
(Developed from NREL's Cost and Scaling model/public data on commercial turbines)
Blade length: | 87 m
Blade mass: | 32 t
Blade deck space: | 256 m^2
Nacelle mass: | 368 t
Nacelle deck space: | 151 m^2
Rotor diamter | 175 m
Rotor mass | 192 t | (blades + hub)
Tower height | 112 m | (same as hub height)
Tower mass | 287 t
Number of sections | 2
Tower section deck space: | 50 m^2

## Monopile parameters
Monopile parameters
Diameter: | 7.2 | m
Length: | 69 | m
Deck space: | 497 | m^2
Mass: | 800 | t
Cost: | 2000 | Euro/t
Transition piece parameters
Deck space: | 100 | m^2
Mass: | 400 | t
Cost: | 2000 | Euro/t

## Array cable parameters
Array cable parameters
Cable voltage: | 66 | kV
Cable current: | 775 | A | (at 2 m burial depth)
Cable size: | 630 | mm^2
Cable density | 45 | kg/m
Cable cost: | 375 | Euro/km
Any assumption around vertical cable length?
Need a site plan?

## Export cable parameters
Export cable parameters
Cable voltage: | 220 | kV
Cable current: | 900 | A
Cable size: | 1000 | mm^2
Cable density | 80 | kg/m
Cable cost: | 550 | Euro/km
Any assumption around vertical cable length?
Need a site plan?

## Substation parameters
Offshore substation parameters
Calculated from NREL's ORBIT model (parameterized by plant capacity)
Assumes two equally sized substations
Topside mass | 1170 | t
Topside cost | 23.4 | M Euro
Substructure mass | 714 | t
Substructure cost | 3.8 | M Euro

## Scour protection
Scour protection parameters
Calculated from NREL's ORBIT model
Cost: | 50 | Euro/tonne
Depth | 1 | m/substructure
Mass | 2500 | tonne/substructure
Total cost: | 4.5 | M Euro
MN: 50 EUR per tonne * 2,500 tonne per turbine * 50 turbines is 6.25m EUR total?
6250000

## Onshore constructin
Onshore construction costs
Estimate includes costs of:
| Building switchyard | (depends on inteconnection voltage)
| Building onshore substation | (depends on interconnection voltage and plant capacity)
| Building transmission line to existing grid connection | (depends on interconnection voltage and distance)
| Miscellaneous costs | (depends on plant capacity)
Cost: | 16.9 | M Euro

## WTIV characteristics
WTIV specifications
Assumed to begin 1st July
Max cargo | 7400 t
Max deckspace | 4000 m^2
Max wind speed (crane) | 15 m/s
Max sign. waveheight (crane) | 2 m
Max windspeed (transit) | 25 m/s
Max significant waveheight (transit) | 3 m
Transit speed (outbound) | 15 km/h
Transit speed (inbound) | 15 km/hr
Day rate | 200K Euro/day
Mobilization cost | 5 days | (at standard day rate)
Waiting on weather day rate | 100% | (of standard day rate)
Note: Cargo and deck space constraints lead to 4 turbine sets per trip
Note: Cargo and deck space constraints lead to 6 monopile+transition piece sets per trip

## Cable lay vessel characteristic
Cable lay vessel characteristics
Assumed to begin 1st July
Max transport sig. wave height: | 2 | m
Max transport wind speed | 25 | m/s
Transit speed | 20 | km/hr
Cable lay speed | 0.2 | km/hr
Max cable storage | 4000 | t | *Note: Updated from 2000 to allow all cable to be installed in 1 trip.
Day rate | 125000 | Euro/day
Mobilization cost | 5 | days
* Use the same vessel parameters for export cables

## OSS heavy lift vessel
Heavy lift vessel specifications
Assumed to begin 1st July
Max wind speed (crane) | 8 m/s
Max sign. waveheight (crane) | 2 m
Max lift (crane) | 5700 t
Max windspeed (transit) | 20 m/s
Max significant waveheight (transit) | 2.5 m
Transit speed | 7 km/hr
Day rate | 325K Euro/day
Mobilization cost | 5 days | (at standard day rate)
Required to lift offshore substation topside
Update 3/31: No longer required if there are two substations

## OSS feeder
Heavy lift vessel specifications
Assumed to begin 1st July
Max cargo | 5000 t
Max deck space | 1000 m^2
Max windspeed (transit) | 25 m/s
Max significant waveheight (transit) | 3 m
Transit speed | 15 km/hr
Day rate | 100K Euro/day
Mobilization cost | 5 days

## Scour vessel
Scour protection vessel specifications
Max cargo: | 6000 | t
Max waveheight (transit) | 2 | m
Max windspeed | 20 | m/s
Transit speed | 6 | km/h
Day rate | 130000 | Euro/day
Mobilization cost | 5 | days | At standard rate
For 2500 tonne/substructure, this vessel can provide scour protection to 2 substructures per trip

## Project plan - turbine install
Times for individual turbine installation processes
*Assumes 4 turbine sets transported per trip | [16 empty] | Aegir Insights input
| Aggregated task | Relations/predecessors [row] | Start time [hours] | End time [hours] | Duration [hr] | Wind speed limit (m/s) | Wave height limit (m) | Time per turbine |  |  | Time per trip |  |  | Total installation time (unweathered) | Total installation time; 1-hour time-step (unweathered) |  | Aegir | Duration (hours) | Wind speed limit (m/s) | Start | End | Time per position | Time per trip | Unweatherd installation time
Mobilize vessel |  |  | 0 | 120 | 120 | [8 empty] | 120 | 120 | assume 1 mobilisation for vessel | Mobilize | 120 | 25 | 0 | 120 |  |  | 120
Time required to fasten 2 tower sections to the vessel |  | 5 | 120 | 122 | 2 | 25 | 3 m swh | Loadout time per turbine | 8 | hr | Total loadout time per trip | 32 | hr | 100 | 100 | assume all 50 turbines loaded-out | Tower loading | 2 | 15 | 120 | 122 | 7.5 | 30 | 100
Time required to fasten the nacelle to the vessel |  | 6 | 122 | 125 | 3 | 25 | 3 m swh | [6 empty] | 150 | 150 |  | Nacelle loading | 2.5 | 15 | 122 | 124.5 |  |  | 125
Time required to fasten 3 blades to the vessel |  | 7 | 125 | 128 | 3 | 25 | 3 m swh | [6 empty] | 150 | 150 |  | Blade loading | 3 | 15 | 124.5 | 127.5 |  |  | 150
Transit to site |  | 8 | 128 | 133 | 5 | 25 |  |  |  |  | Transit time per trip | 5 | hr | 65 | 65 | assume 13 trips to site (12 trips * 4 turbines plus 1 trip * 2 turbines) | Transit to site | 8.27 | 25 | 127.5 | 135.77 | 2.0675 | 8.27 | 103.375 | (120 km and vessel speed 15 km/h)
Time required to position vessel at site | Positioning/jackup/preloading | 9 | 133 | 138 | 5 | 25 | 2 m swh | Install time per turbine | 26 | hr | Total install time per trip | 104 | hr | 250 | 250 | assume all 50 turbines are installed | Postioning / Jackup / Preloading | 6 | 25 | 135.77 | 141.77 | 20 | 80 | 300
Time for vessel to jackup |  | 10 | 138 | 140 | 2 | 25 | 2 m swh | [6 empty] | 100 | 100 |  | Tower installation | 2 | 15 | 141.77 | 143.77 |  |  | 100
Time required to release the a tower section from the vessel | Tower installation | 11 | 140 | 140 | 0 | 15 | 2 m swh | [6 empty] | 0 | 0 |  | Nacelle installation | 3 | 15 | 143.77 | 146.77 |  |  | 150
Time required to lift tower section |  | 12 | 140 | 141 | 1 | 15 | 2 m swh | [6 empty] | 50 | 50 |  | Blade installation | 9 | 15 | 146.77 | 155.77 |  |  | 450
Time required to attach the turbine tower to the transition piece |  | 13 | 141 | 142 | 1 | 15 | 2 m swh | [6 empty] | 50 | 50 |  | Aegir | Duration (hours) | Wind speed limit (m/s) | 155.77 | #VALUE! |  |  | #VALUE!
Time required to release the a tower section from the vessel |  | 14 | 142 | 142 | 0 | 15 | 2 m swh | [6 empty] | 0 | 0 |  | Mobilize | -19.2756 | 15.8333 | #VALUE! | #VALUE! | -4.8189 | -19.2756 | -240.9444
Time required to lift tower section |  | 15 | 142 | 143 | 1 | 15 | 2 m swh | [6 empty] | 50 | 50 |  | Tower loading | -26.5922 | 15.3333 | #VALUE! | #VALUE! | -6.6481 | -26.5922 | -332.4028
Time required to attach the turbine tower to the transition piece |  | 16 | 143 | 144 | 1 | 15 | 2 m swh | [6 empty] | 50 | 50 |  | Nacelle loading | -33.9089 | 14.8333 |  | Sums | 18.1006 | 72.4022 | #VALUE!
Time required to re-equip crane | Nacelle installation | 17 | 144 | 145 | 1 | 15 | 2 m swh | [6 empty] | 50 | 50
Time required to release the nacelle from the vessel |  | 18 | 145 | 145 | 0 | 15 | 2 m swh | [6 empty] | 0 | 0 | [5 empty] | Unweathered installation days |  |  | #VALUE!
Time required to lift nacelle |  | 19 | 145 | 146 | 1 | 15 | 2 m swh | [6 empty] | 50 | 50 | [5 empty] | Unweathered installation days per position |  |  | #VALUE!
Time required to attach the nacelle to the turbine tower |  | 20 | 146 | 147 | 1 | 15 | 2 m swh | [6 empty] | 50 | 50
Time required to re-equip crane | Blade installation | 21 | 147 | 148 | 1 | 15 | 2 m swh | [6 empty] | 50 | 50
Time required to release the turbine blade from the vessel |  | 22 | 148 | 148 | 0 | 15 | 2 m swh | [6 empty] | 0 | 0
Time required to lift turbine blade |  | 23 | 148 | 149 | 1 | 15 | 2 m swh | [6 empty] | 50 | 50
Tie required to attache the turbine blade to the nacelle |  | 24 | 149 | 151 | 2 | 15 | 2 m swh | [6 empty] | 100 | 100
Time required to release the turbine blade from the vessel |  | 25 | 151 | 151 | 0 | 15 | 2 m swh | [6 empty] | 0 | 0
Time required to lift turbine blade |  | 26 | 151 | 152 | 1 | 15 | 2 m swh | [6 empty] | 50 | 50
Tie required to attache the turbine blade to the nacelle |  | 27 | 152 | 154 | 2 | 15 | 2 m swh | [6 empty] | 100 | 100
Time required to release the turbine blade from the vessel |  | 28 | 154 | 154 | 0 | 15 | 2 m swh | [6 empty] | 0 | 0
Time required to lift turbine blade |  | 29 | 154 | 155 | 1 | 15 | 2 m swh | [6 empty] | 50 | 50
Tie required to attache the turbine blade to the nacelle |  | 30 | 155 | 157 | 2 | 15 | 2 m swh | [6 empty] | 100 | 100
Time required to jackdown |  | 31 | 157 | 159 | 2 | 25 | 2 m swh | [6 empty] | 100 | 100
Transit to port |  | 32 |  |  | 5 | 25 | 3 m swh |  |  |  | Transit time per trip | 5 | hr | 65 | 65 | assume 13 return trips to port (12 trips * 4 turbines plus 1 trip * 2 turbines)
[12 empty] | Total installation time (days) |  | 81.25 | 81.25

## Project plan - monopile install
Times for individual turbine installation processes
*Assumes 6 turbine sets transported per trip
| Relations/predecessors [row] | Start time [hours] | End time [hours] | Duration [hr] | Wind speed limit (m/s) | Wave height limit (m) | Time per monopile |  |  | Time per trip |  |  | Total installation time (unweathered) | Total installation time; 1-hour time-step (unweathered)
Mobilize vessel |  | 0 | 120 | 120 | [8 empty] | 120 | 120 | assume 1 mobilisation for vessel
Fasten monopile to vessel | 5 | 120 | 132 | 12 | 25 | 3 | Loadout time per monopile | 20 | hr | Total loadout time per trip | 120 | hr | 600 | 600 | assume all 50 monopiles loaded-out
Fasten transition piece to vessel | 6 | 132 | 140 | 8 | 25 | 3 | [6 empty] | 400 | 400
Transit to site | 7 | 140 | 145 | 5 | 25 | 3 |  |  |  | Transit time per trip | 5 | hr | 45 | 45 | assuming 9 trips: 8*6 MPs + 1*2 MPs
Position vessel onsite | 8 | 145 | 147 | 2 | 25 | 2 | Install time per monopile/transition piece pair | 18 | hr | Total install time per trip | 108 | hr | 100 | 100 | assume all 50 monopiles installed
ROV survey of seabed | 9 | 147 | 148 | 1 | 25 | 2 | [6 empty] | 50 | 50
Release monopile from vessel | 10 | 148 | 151 | 3 | 25 | 2 | [6 empty] | 150 | 150
Lower monopile to seabed | 11 | 151 | 152 | 1 | 15 | 2 | [6 empty] | 50 | 50
Re-equip crane with hydraulic hammer | 12 | 152 | 153 | 1 | 15 | 2 | [6 empty] | 50 | 50
Drive monopile into seabed | 13 | 153 | 155 | 2 | 15 | 2 | [6 empty] | 100 | 100
Re-equip crane | 14 | 155 | 156 | 1 | 25 | 2 | [6 empty] | 50 | 50
Release transition piece from vessel | 15 | 156 | 158 | 2 | 25 | 2 | [6 empty] | 100 | 100
Lift transition piece | 16 | 158 | 159 | 1 | 15 | 2 | [6 empty] | 50 | 50
Bolt transition piece to monopile | 17 | 159 | 163 | 4 | 15 | 2 | [6 empty] | 200 | 200
Transit to site | 18 |  |  | 5 | 25 | 3 |  |  |  | Transit time per trip | 5 | hr | 45 | 45 | assuming 9 return trips
[11 empty] | Total installation time (days) |  | 87.9167 | 87.9167

## Project plan - array cable inst
Times for array cable installation processes
* Assumes all cable carried/laid/buried in a single trip
| Relations/predecessors [row] | Start time [hours] | End time [hours] | Duration [hr] | Wind speed limit (m/s) | Wave height limit (m) | Time per turbine |  |  | Total project time |  |  | Total installation time (unweathered) | Total installation time; 1-hour time-step (unweathered)
Mobilize vessel |  | 0 | 120 | 120 | [8 empty] | 120 | 120 | assume 1 mobilisation for vessel
Load cable at port | 5 | 120 | 126 | 6 | 25 | 2 | [6 empty] | 6 | 6 | assume a single load-out of cable
Transit to site | 6 | 126 | 133 | 7 | 25 | 2 | [6 empty] | 7 | 7 | assume a single trip to site
Position onsite | 7 | 133 | 135 | 2 | 25 | 2 | Cable prep and lay per turbine | 36 | hr | Total time | 1800 | hr | 100 | 100 | assume all 50 cables installed
Prepare cable | 8 | 135 | 136 | 1 | 25 | 2 | [6 empty] | 50 | 50
Pull in cable at turbine | 9 | 136 | 142 | 6 | 25 | 2 | [6 empty] | 300 | 300
Terminate cable | 10 | 142 | 148 | 6 | 25 | 2 | [6 empty] | 300 | 300
Lower cable to seafloor | 11 | 148 | 149 | 1 | 25 | 2 | [6 empty] | 50 | 50
Lay/bury cable to next turbine in string | 12 | 149 | 156 | 7 | 25 | 2 | [6 empty] | 350 | 350
Prepare cable | 8 | 156 | 157 | 1 | 25 | 2 | [6 empty] | 50
Pull in cable at turbine | 9 | 157 | 163 | 6 | 25 | 2 | [6 empty] | 300
Terminate cable | 10 | 163 | 169 | 6 | 25 | 2 | [6 empty] | 300
Transit to port |  |  |  | 7 | 25 | 2 | [6 empty] | 7 | 7 | assume a single return trip to port
[11 empty] | Total installation time (days) |  | 80.8333 | 53.75

## Project plan - export cable ins
Times for export cable installation processes
* Assumes all cable carried/laid/buried in a single trip
| Relations/predecessors [row] | Start time [hours] | End time [hours] | Duration [hr] | Wind speed limit (m/s) | Wave height limit (m) | Total time per cable |  |  | Total project time |  |  | Total installation time (unweathered) | Total installation time; 1-hour time-step (unweathered)
Mobilize vessel |  | 0 | 120 | 120 | [10 empty] | assume 1 mobilisation for vessel
Load cable at port | 5 | 120 | 126 | 6 | 25 | 2 | [8 empty] | assume a single load-out of cable
Position at landfall | 7 | 126 | 128 | 2 | 25 | 2 | Cable prep and lay total | 241 | hr | Total time | 482 | hr |  |  | assume all 50 cables installed
Prepare cable | 8 | 128 | 129 | 1 | 25 | 2
Pull in cable | 9 | 129 | 135 | 6 | 25 | 2
Lower cable to seafloor | 11 | 135 | 136 | 1 | 25 | 2
Lay/bury cable to offshore substation | 12 | 136 | 361 | 225 | 25 | 2
Terminate cable | 10 | 135 | 141 | 6 | 25 | 2
Transit to port |  |  |  | 7 | 25 | 2 | [8 empty] | assume a single return trip to port
Total installation time (days)

## Project plan - OSS install
Times for substation installation process
*Assumes two OSS at site
*Assume feeder barge transports alongside WTIV
| Relations/predecessors [row] | Start time [hours] | End time [hours] | Duration [hr] | Wind speed limit (m/s) | Wave height limit (m) | Time per substation |  |  | Time per trip |  |  | Total installation time (unweathered)
[13 empty] | 0 | assume 1 mobilisation for vessel
Assume vessel mobilisation and load out carried out for foundation installation | [12 empty] | 0 | assume all 50 monopiles loaded-out
Fasten monopile |  | 0 | 12 | 12 | 25 | 3
Fasten topside | 8 | 12 | 24 | 12 | 25 | 3 | [6 empty] | 600
Transit to site | 7 | 24 | 29 | 5 | 25 | 2 |  |  |  | Transit time per trip | 5 | hr | 5 | assuming 9 trips: 8*6 MPs + 1*2 MPs
Position vessel onsite | 8 | 29 | 31 | 2 | 25 | 2 | Install time per substation | 29.5 | hr | Total install time per trip | 29.5 | hr | 2 | assume all 50 monopiles installed
ROV survey of seabed | 9 | 31 | 32 | 1 | 25 | 2 | [6 empty] | 1
Release monopile from vessel | 10 | 32 | 35 | 3 | 25 | 2 | [6 empty] | 3
Lower monopile to seabed | 11 | 35 | 36 | 1 | 15 | 2 | [6 empty] | 1
Re-equip crane with hydraulic hammer | 12 | 36 | 37 | 1 | 15 | 2 | [6 empty] | 1
Drive monopile into seabed | 13 | 37 | 38.5 | 1.5 | 15 | 2 | [6 empty] | 1.5
Re-equip crane | 14 | 38.5 | 39.5 | 1 | 25 | 2 | [6 empty] | 1
Release transition piece from vessel | 15 | 39.5 | 41.5 | 2 | 25 | 2 | [6 empty] | 2
Lift transition piece | 16 | 41.5 | 42.5 | 1 | 15 | 2 | [6 empty] | 1
Bolt transition piece to monopile | 17 | 42.5 | 46.5 | 4 | 15 | 2 | [6 empty] | 4
Lift substation topside | 18 | 46.5 | 54.5 | 8 | 15 | 2
Bolt topside to transition piece | 19 | 54.5 | 58.5 | 4 | 15 | 2
Transit to site | 18 |  |  | 5 | 25 | 2 |  |  |  | Transit time per trip | 5 | hr | 5 | assuming 9 return trips
[11 empty] | Total installation time (days) |  | 26.1458

## Project plan - scour protection
Times for scour protection installation process
| Relations/predecessors [row] | Start time [hours] | End time [hours] | Duration [hr] | Wind speed limit (m/s) | Wave height limit (m) | Time per substructure |  |  | Time per trip |  |  | Total installation time (unweathered)
Mobilize vessel |  | 0 | 168 | 168 | [8 empty] | 168 | assume 1 mobilisation for vessel
Load rocks at port | 5 | 168 | 172 | 4 | 25 | 3 |  |  |  | Transit time per trip | 40 | hr | 4 | assuming 25 trips
Transit to site | 6 | 172 | 192 | 20 | 20 | 2 | Scour protection time per substructure | 10.25 | hr | Total install time per trip | 20.25 | hr | 20
Dump rocks at substructure |  | 192 | 202 | 10 | 20 | 2 | [6 empty] | 10
Transit to next turbine |  | 202 | 202.25 | 0.25 | 20 | 2 | [6 empty] | 0.25
Dump rocks at substructure |  | 202.25 | 212.25 | 10 | 20 | 2 | [6 empty] | 10
Transit to port |  | 212.25 | 232.25 | 20 | 20 | 2 | [6 empty] | 20
[11 empty] | Total installation time (days) |  | 9.6771

## Output comparisons
MODEL OUTPUT COMPARISON
PROJECT BALANCE-OF-SYSTEM COSTS
Model | Project CAPEX (M. Euros) | Relative error
ORBIT
OREC
DTU
Fraunhofer
Strathclyde
Aegir
COMPONENT COSTS (Capital + installation)
|  |  | Turbine | [5 empty] | * Turbine CAPEX only includes installation costs
Model | Total (M. Euros) | Relative error | Capital cost (M. Euros) | Relative error | Installation cost (M. Euros) | Relative error | Installation time (days) | Relative error | Waiting on weather time (days) | Relative error | Waiting on weather cost (M. Euros) | Relative error
ORBIT | 39.8 |  | N/A |  | 20.2 |  | 81.8 |  | 3.9 |  |  |  | *Reset transit wave height limits to 2m. INclude mobilization time
OREC | 498.2 |  | 460 | N/A | 18.3 | -4.0201 | 81 | 21.4765 | 13 |  | 2.6
DTU
Fraunhofer |  |  |  |  | 17.07 | -15.495 | 85.37 | 4.3643 | 4.12 |  | 0.82 |  | *using the updated project plan
BVG
Strathclyde | N/A | N/A | N/A | N/A | 35.08 | 73.6634 | 175.4 | 114.4254 | 16.517 |  | 3.3034
Aegir | 399.22 |  | 365.4 |  | 33.82 | 67.4257 | 98.49 | 20.4034 | 6.32 |  | 1.264 |  | Start of installation early summer / Own assumptions on duration of installation steps / incl Weather Downtime
|  |  | Foundation | [11 empty] | * Assume monopile/TP are installed simultaneously by same vessel
Model | Total (M. Euros) | Relative error | Capital cost (M. Euros) | Relative error | Installation cost (M. Euros) | Relative error | Installation time for MP(days) | Relative error | Installation time for TP(days) | Relative error | Waiting on weather time (days) | Relative error | Waiting on weather cost (M. Euros) | Relative error
ORBIT | 143.7 |  | 120 |  | 19.5 |  | 92.7 |  | Included |  | 5.1 |  |  |  | *Reset transit wave limits to 2 m
OREC | 141.05 |  | 120 |  | 19.2 | -18.9873 | 86 | -1.6018 | No additional days |  | 9 |  | 0.6 |  | 7 days transit + 1 downtime; 79 days installation + 12 downtime
DTU
Fraunhofer |  |  |  |  | 18.26 | -6.359 | 91.29 | -1.521 | included |  | 3.37 |  | 0.67
BVG
Strathclyde | N/A | N/A | N/A | N/A | 18.01 | -7.641 | 90.05 | -2.8587 |  |  | 1.65 |  | 0.33
Aegir |  |  | 120 |  | 84.5 | 333.3333 | 92.2 | -0.53937 | 80.2 |  | 11.7 |  | N/A |  | Second vessel to install transition pieces / full cycle around: 92.2 days / incl. weather downtime, mob, demob etc.
Array cables
Model | Total (M. Euros) | Relative error | Capital cost (M. Euros) | Relative error | Installation cost (M. Euros) | Relative error | Installation time (days) | Relative error | Waiting on weather time (days) | Relative error | Waiting on weather cost (M. Euros) | Relative error
ORBIT | 44.9 |  | 26 |  | 9.9 |  | 74.9 |  | 2.9 |  |  |  | 84.5 km of cable
OREC | 40.32 |  | 29.65 |  | 11.2 |  | 79.7 |  | 3.9 |  | 0.5 |  | Installation cost excluding onshore facilities
DTU
Fraunhofer |  |  |  |  | 6.87 | -30.6061 | 54.97 | -26.6088 | 1.22 |  | 0.15
BVG
Strathclyde | N/A | N/A | N/A | N/A | 7.5 | -24.2424 | 60 | -19.8932 | 0 |  | 0 |  | (negligible weather delays at 25m/s & 2m)
Aegir |  |  | 44.79 | 72.2692 | 15.63 | 57.8788 | 83.73 | 11.7891 | 15.81 |  | 1.9763
Export cables
Model | Total (M. Euros) | Relative error | Capital cost (M. Euros) | Relative error | Installation cost (M. Euros) | Relative error | Installation time (days) | Relative error | Waiting on weather time (days) | Relative error | Waiting on weather cost (M. Euros) | Relative error
ORBIT | 70 |  | 49.5 |  | 3.5 |  | 22.5 |  | 0
OREC | 50.24 |  | 46.2 |  | 3.9 | -80.2927 | 21.2 |  | 0.6 |  | 0.07
DTU
Fraunhofer |  |  |  |  | 3.27 | -6.5714 | 26.17 | 16.3111 | 0.55 |  | 0.07
BVG
Strathclyde |  |  |  |  | 3.125 |  | 25 |  | 0 |  | 0
Aegir |  |  | 49.5 |  | 22 | 528.5714 | N/A |  | N/A |  | N/A
Offshore substation
Model | Total (M. Euros) | Relative error | Capital cost (M. Euros) | Relative error | Installation cost (M. Euros) | Relative error | Installation time (days) | Relative error | Waiting on weather time (days) | Relative error | Waiting on weather cost (M. Euros) | Relative error
ORBIT | 76.2 |  | 73.9 |  | 2 |  | 5.1 |  | 1.2
OREC | 56.3 |  | 54.4 |  | 1.9 |  | 8 |  | 0.1 |  | 0.1
DTU
Fraunhofer |  |  |  |  | 1.62 |  | 5.41 |  | 0.12 |  | 0.03 |  | *assumed cost of 300k€ (WTIV: 200k€ + Feeder: 100k€) * result with OSS heavy lift (325k€) & Feeder (100k€): Inst. Cost = 2.3M€ & WoWCost = 0.05M€
BVG
Strathclyde |  |  |  |  | 1.6478 |  | 5.07 |  | 0.05 |  | 0.01625
Aegir (1) | 60 |  | 50 |  | 10 |  | N/A |  | N/A |  | N/A
Onshore construction/substation
Model | Total (M. Euros) | Relative error | Capital cost (M. Euros) | Relative error | Installation cost (M. Euros) | Relative error | Installation time (days) | Relative error | Waiting on weather time (days) | Relative error | Waiting on weather cost (M. Euros) | Relative error
ORBIT | 16.9
OREC
DTU
Fraunhofer
BVG
Strathclyde
Aegir (1) | 30 |  | 20 |  | 10 |  | N/A |  | N/A |  | N/A |  | One onshore substation
Scour protection
Model | Total (M. Euros) | Relative error | Capital cost (M. Euros) | Relative error | Installation cost (M. Euros) | Relative error | Installation time (days) | Relative error | Waiting on weather time (days) | Relative error | Waiting on weather cost (M. Euros) | Relative error
ORBIT | 16.5 |  | 4.5 |  | 8 |  | 71.1 |  | 2.5
OREC |  |  | 6.25
DTU
Fraunhofer |  |  |  |  | 9.83 |  | 75.61 |  | 3.68 |  | 0.48
BVG
Strathclyde
Aegir (1) |  |  | 2.318 | -48.4889 | 5.892 | -26.35 | N/A |  | N/A |  | N/A
Project development
Model | Total (M. Euros) | Relative error | Capital cost (M. Euros) | Relative error | Installation cost (M. Euros) | Relative error | Installation time (days) | Relative error | Waiting on weather time (days) | Relative error | Waiting on weather cost (M. Euros) | Relative error
ORBIT
OREC
DTU
Fraunhofer
BVG
Strathclyde
Aegir (1)
COST BREAKDOWNS
Cabling
Model | Array cable length (km) | Relative error
ORBIT | 104
OREC | 80
DTU
Fraunhofer | 100
BVG
Strathclyde
Aegir | 79.15
Model | Export cable length (km) | Relative error
ORBIT | 91
OREC | 179 |  | Assume two cables (so 90km each, onshore + offshore)
DTU
Fraunhofer | 90
BVG
Strathclyde
Aegir | 90
Model | Average turbine install time (days/WTG) | Relative error
ORBIT | 2.5
OREC | 1.7083 |  | Excluding weather
DTU
Fraunhofer | 2.4
BVG
Strathclyde
Aegir | 1.97 |  | see Turbine CAPEX line: based on own duration assumptions
Model | Average monopile install time (days/monopile) | Relative error
ORBIT | 1.6
OREC | 1
DTU
Fraunhofer | 1.5 |  | *monopile & TP with weather and grouting
BVG
Strathclyde
Aegir | 3.44 |  | MP + TP install (two vessels simultaneously working: cycle with 92 days)
Other budget items outside of budget structure above
Model | Travel | Construction resources | Operations prep | Construction Management | Insurances | Contingency
Aegir | 1.728 | 34.37 | 10 | 13.23 | 7.45 | 42
OREC (£m) |  |  |  |  | 18 | 122
Note on H14: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Incl WoW
Note on H23: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Incl WoW
Note on H32: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Incl WoW
Note on D41: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Offshore cable only

## Component sizing comparisons
Comparison of component sizing tools
Monopile
| Mass [t] | Length [m] | Diameter [m] | Cost per monopile[M Euros]
ORBIT | 689 | 64.8 | 8.5 | 1.378
OREC | 962 |  |  | 1.925 | Monopile only, excluding TP and secondary steel
DTU
Transition piece
| Mass [t] | Length [m] | Diameter [m] | Cost per TP [M Euros]
ORBIT | 324 | 25 | 8.7 | 0.648
OREC | 300 |  |  | 0.8
DTU
Array cables
| Length [km] | Cost [M Euros]
ORBIT | 62 | 23.4 | 5 Strings. Includes substation connections (not computed separatley). Assume ring config
OREC | 55 | 19.5 | 42km strings + 13km substation connections
DTU
Export cables
| Length [km] | Number of cables | Cost [M Euros]
ORBIT | 45 | 2 | 49.5 |  | Includes the 3km onshore cables; does not include onshore construction costs (~100M)
OREC | 42 | 2 |  | 84km total | Plus two 3km onshore cables
DTU
Offshore substation
| Topside mass | Monopile mass | Overall cost [M Euros]
ORBIT | 1170 | 714 | 118.4
OREC |  |  |  | N/A
DTU